# Protocol for the Profibus Communication between the Beam Inhibit System (BIS) and the PITZ Control System (CS)

The FDL-Profibus Protocol is handled at the SPS via the Functions AG_SEND and AG_RECEIVE from the SIMATIC-NET library. PB-address of BIS- SPS is 10, LSAP is 11. The communication with the control system is realized via unspecified FDL connection ( free layer 2 access ),  that’s why address of the remote station is written in the first 4 bytes of the data blocks. These 4 bytes are cut during receiving of DB20 or added during sending of  DB30 from the CS.

There are two directions of communication: BIS_2_CS and CS_2_BIS.

### BIS_2_CS

When in running mode, the SPS will try to send a data block to the CS every 2 seconds. The one and only data block is the status data block. It contains information about the screens, the valves, end switches and the beam modes.

The status data block has a length of 32 byte and the following structure:

The description of the meaning of the status register bits can be found in symbol table of the SPS-program.

### CS_2_BIS

The CS can send data blocks of max. 32 bytes to the SPS containing commands for the BIS to set masks and start / stop beam. If the SPS is in running mode it will try to receive such blocks via Profibus. The most of these commands are only 4 bytes long.

The first word (2 bytes) has to contain the command itself, the second one a parameter that can be TRUE or FALSE. For fail save operation the ASCII-value of the command and parameter letter has to be accompanied by its ones-complement in the high-byte of the word.

The following commands are implemented:

| Command Letter | Parameter | 1. word | 2. word | description |
| --- | --- | --- | --- | --- |
| S (tart beam) | T (rue) | 0xAC53 | 0xAB54 | Reset Beam Stop FF |
| S (top beam) | F (alse) | 0xAC53 | 0xB946 | Set Beam Stop FF |
| M (ask set) | T | 0xB24D | 0xAB54 | Set mask |
| M (ask reset) | F | 0xB24D | 0xB946 | Reset mask |

*)	The data block of the Mask command consists of the two words shown above and additional data, that has to be written into the SPS. In this case the 4 byte mask block  has to follow.

Received data blocks with anything else than defined commands in the two first words (corresponding to the table) will be ignored.

Received data blocks with anything else than defined commands in the two first words (corresponding to the table) will be ignored.

In detail the input, status, mask and output bits have the following meaning:

inputs					Byte

S_BIT_1.I	raddiation & interl ok	E       4.0	0.0	BOOL	inputs, DB20 +4.0, MD30

D_BIT_1.I1	vacuum valve 1 closed	E       4.1	0.1	BOOL

D_BIT_1.I2	vacuum valve 1 open	E       4.2	0.2	BOOL

D_BIT_2.I1	vacuum valve 2 closed	E       4.3	0.3	BOOL

D_BIT_2.I2	vacuum valve 2 open	E       4.4	0.4	BOOL

D_BIT_3.I1	vacuum valve 3 closed	E       4.5	0.5	BOOL

D_BIT_3.I2	vacuum valve 3 open	E       4.6	0.6	BOOL

D_BIT_4.I1	vacuum valve 4 closed	E       4.7	0.7	BOOL

D_BIT_4.I2	vacuum valve 4 open	E       5.0	1.0	BOOL

S_BIT_2.I	laser shutter 1 closed	E       5.1	1.1	BOOL

S_BIT_3.I	pressurised air ok		E       5.2	1.2	BOOL

D_BIT_5.I1	vacuum valve 6 closed	E       5.3	1.3	BOOL

D_BIT_5.I2	vacuum valve 6 open	E       5.4	1.4	BOOL

S_BIT_4.I	dipole on		E       5.5	1.5	BOOL

D_BIT_6.I1	mirror to pepperpot in	E       5.6	1.6	BOOL

D_BIT_6.I2	mirror to pepperpot out	E       5.7	1.7	BOOL

D_BIT_7.I1	mirror to cathode in	E       6.0	2.0	BOOL

D_BIT_7.I2	mirror to cathode out	E       6.1	2.1	BOOL

D_BIT_8.I1	far cup screen in		E       6.2	2.2	BOOL

D_BIT_8.I2	far cup screen out	E       6.3	2.3	BOOL

D_BIT_9.I1	viewscreen inj in		E       6.4	2.4	BOOL

D_BIT_9.I2	viewscreen inj out	E       6.5	2.5	BOOL

D_BIT_10.I1	viewscreen ana in	E       6.6	2.6	BOOL

D_BIT_10.I2	viewscreen ana out	E       6.7	2.7	BOOL

D_BIT_11.I1	viewscreen image PP in	E       7.0	3.0	BOOL

D_BIT_11.I2	viewscreen image PP out	E       7.1	3.1	BOOL

D_BIT_12.I1	mirror image PP in	E       7.2	3.2	BOOL

D_BIT_12.I2	mirror image PP out	E       7.3	3.3	BOOL

S_BIT_5.I	cathode lin out		E       7.4	3.4	BOOL

S_BIT_6.I	cathode lat out		E       7.5	3.5	BOOL

S_BIT_7.I	beam stop button		E       7.6	3.6	BOOL

S_BIT_8.I	solenoid supply ok	E       7.7	3.7	BOOL

maskbits

D_BIT_1.M	mask vac valve 1		M      38.0	4.0	BOOL	masks, DB20 +8.0, MD38

D_BIT_2.M	mask vac valve 2		M      38.1	4.1	BOOL

D_BIT_3.M	mask vac valve 3		M      38.2	4.2	BOOL

D_BIT_4.M	mask vac valve 4		M      38.3	4.3	BOOL

D_BIT_5.M	mask vac valve 6		M      38.5	4.5	BOOL

S_BIT_4.M	mask dipole on		M      38.6	4.6	BOOL

D_BIT_6.M	mask mirror to pp	M      38.7	4.7	BOOL

D_BIT_7.M	mask mirror to cath	M      39.0	5.0	BOOL

D_BIT_8.M	mask far cup screen	M      39.1	5.1	BOOL

D_BIT_9.M	mask viewscreen inj	M      39.2	5.2	BOOL

D_BIT_10.M	mask viewscreen ana	M      39.3	5.3	BOOL

D_BIT_11.M	mask screen image PP	M      39.4	5.4	BOOL

D_BIT_12.M	mask mirror image PP	M      39.5	5.5	BOOL

S_BIT_8.M	mask gun solen supply ok	M      39.6	5.6	BOOL

S_BIT_2.M	mask laser shutt 1	M      39.7	5.7	BOOL

S_BIT_3.M	mask pressurised air ok	M      40.1	6.1	BOOL

S_BIT_5.M	mask cath lin		M      40.3	6.3	BOOL

S_BIT_6.M	mask cath lat		M      40.4	6.4	BOOL

internal statusbits

valves ok		M      34.0	8.0	BOOL	intern statusbits, DB20 +12.0, MD34

sensor not o.k.		M      34.1	8.1	BOOL	"

PBs2bok		M      34.3	8.2	BOOL	Profibus seems to be ok.

BISfaultFlag		M      34.4	8.3	BOOL	set by OB81

PBsent			M      34.5	8.4	BOOL	set 1 if sent done

err_PBsend		M      34.6	8.5	BOOL	Error during Profibus Transmission

err_PBrec		M      34.7	8.6	BOOL	Error during Profibus Receive

PBrecd			M      35.0	8.7	BOOL

PBrun			M      35.1	9.0	BOOL

stop beam pulse		M      35.2	9.1	BOOL	1 sec pulse

start beam pulse		M      35.3	9.2	BOOL	1 sec pulse

#### outputs

O_BIT.1    repetition rate 1 Hz	A       8.0	12.0	BOOL	to Laser, outputs, DB20 +16.0, MD42

O_BIT.2    repetition rate 10 Hz	A       8.1	12.1	BOOL	to CS

O_BIT.3    pulse length 50 µs	A       8.2	12.2	BOOL	to CS

O_BIT.4    pulse length 800 µs	A       8.3	12.3	BOOL	to CS

O_BIT.5    op-mode cond set	A       8.4	12.4	BOOL	to CS

O_BIT.6    op-mode gun set	A       8.5	12.5	BOOL	to CS

O_BIT.7    op-mode analyse set	A       8.6	12.6	BOOL	to CS

O_BIT.8    op-mode injector set	A       8.7	12.7	BOOL	to CS

O_BIT.9    op-mode UV laser set	A       9.0	13.0	BOOL	to CS

O_BIT.10  op-mode PP align set	A       9.1	13.1	BOOL	to CS

O_BIT.11  RF enable		A       9.2	13.2	BOOL	to CS

O_BIT.12   L-shutter enable	A       9.3	13.3	BOOL	to Laser

O_BIT.13   Beam Stop		A       9.4	13.4	BOOL	to CS