## Sheet1
PITZ | Beam inhibit system variables |  |  | 2026-07-28 18:59
DOOCS-variable name | description
inputs
S_BIT_1.I | raddiation & interl ok | E 4.0 | 0.0 | BOOL | inputs, DB20 +4.0, MD30
D_BIT_1.I1 | vacuum valve 1 closed | E 4.1 | 0.1 | BOOL
D_BIT_1.I2 | vacuum valve 1 open | E 4.2 | 0.2 | BOOL
D_BIT_2.I1 | vacuum valve 2 closed | E 4.3 | 0.3 | BOOL
D_BIT_2.I2 | vacuum valve 2 open | E 4.4 | 0.4 | BOOL
D_BIT_3.I1 | vacuum valve 3 closed | E 4.5 | 0.5 | BOOL
D_BIT_3.I2 | vacuum valve 3 open | E 4.6 | 0.6 | BOOL
D_BIT_4.I1 | vacuum valve 4 closed | E 4.7 | 0.7 | BOOL
D_BIT_4.I2 | vacuum valve 4 open | E 5.0 | 1.0 | BOOL
S_BIT_2.I | laser shutter 1 closed | E 5.1 | 1.1 | BOOL
S_BIT_3.I | pressurised air ok | E 5.2 | 1.2 | BOOL
D_BIT_5.I1 | vacuum valve 6 closed | E 5.3 | 1.3 | BOOL
D_BIT_5.I2 | vacuum valve 6 open | E 5.4 | 1.4 | BOOL
S_BIT_4.I | dipole on | E 5.5 | 1.5 | BOOL
D_BIT_6.I1 | mirror to pepperpot in | E 5.6 | 1.6 | BOOL
D_BIT_6.I2 | mirror to pepperpot out | E 5.7 | 1.7 | BOOL
D_BIT_7.I1 | mirror to cathode in | E 6.0 | 2.0 | BOOL
D_BIT_7.I2 | mirror to cathode out | E 6.1 | 2.1 | BOOL
D_BIT_8.I1 | far cup screen in | E 6.2 | 2.2 | BOOL
D_BIT_8.I2 | far cup screen out | E 6.3 | 2.3 | BOOL
D_BIT_9.I1 | viewscreen inj in | E 6.4 | 2.4 | BOOL
D_BIT_9.I2 | viewscreen inj out | E 6.5 | 2.5 | BOOL
D_BIT_10.I1 | viewscreen ana in | E 6.6 | 2.6 | BOOL
D_BIT_10.I2 | viewscreen ana out | E 6.7 | 2.7 | BOOL
D_BIT_11.I1 | viewscreen image PP in | E 7.0 | 3.0 | BOOL
D_BIT_11.I2 | viewscreen image PP out | E 7.1 | 3.1 | BOOL
D_BIT_12.I1 | mirror image PP in | E 7.2 | 3.2 | BOOL
D_BIT_12.I2 | mirror image PP out | E 7.3 | 3.3 | BOOL
S_BIT_5.I | cathode lin out | E 7.4 | 3.4 | BOOL
S_BIT_6.I | cathode lat out | E 7.5 | 3.5 | BOOL
S_BIT_7.I | beam stop button | E 7.6 | 3.6 | BOOL
S_BIT_8.I | solenoid supply ok | E 7.7 | 3.7 | BOOL
maskbits
D_BIT_1.M | mask vac valve 1 | M 38.0 | 4.0 | BOOL | masks, DB20 +8.0, MD38
D_BIT_2.M | mask vac valve 2 | M 38.1 | 4.1 | BOOL
D_BIT_3.M | mask vac valve 3 | M 38.2 | 4.2 | BOOL
D_BIT_4.M | mask vac valve 4 | M 38.3 | 4.3 | BOOL
D_BIT_5.M | mask vac valve 6 | M 38.5 | 4.5 | BOOL
S_BIT_4.M | mask dipole on | M 38.6 | 4.6 | BOOL
D_BIT_6.M | mask mirror to pp | M 38.7 | 4.7 | BOOL
D_BIT_7.M | mask mirror to cath | M 39.0 | 5.0 | BOOL
D_BIT_8.M | mask far cup screen | M 39.1 | 5.1 | BOOL
D_BIT_9.M | mask viewscreen inj | M 39.2 | 5.2 | BOOL
D_BIT_10.M | mask viewscreen ana | M 39.3 | 5.3 | BOOL
D_BIT_11.M | mask screen image PP | M 39.4 | 5.4 | BOOL
D_BIT_12.M | mask mirror image PP | M 39.5 | 5.5 | BOOL
S_BIT_8.M | mask gun solen supply ok | M 39.6 | 5.6 | BOOL
S_BIT_2.M | mask laser shutt 1 | M 39.7 | 5.7 | BOOL
S_BIT_3.M | mask pressurised air ok | M 40.1 | 6.1 | BOOL
S_BIT_5.M | mask cath lin | M 40.3 | 6.3 | BOOL
S_BIT_6.M | mask cath lat | M 40.4 | 6.4 | BOOL
internal statusbits
SBIT_1_0 | valves ok | M 34.0 | 8.0 | BOOL | intern statusbits, DB20 +12.0, MD34
SBIT_1_1 | sensor not o.k. | M 34.1 | 8.1 | BOOL | "
SBIT_1_2 | PBs2bok | M 34.3 | 8.2 | BOOL | Profibus seems to be ok.
SBIT_1_3 | BISfaultFlag | M 34.4 | 8.3 | BOOL | set by OB81
SBIT_1_4 | PBsent | M 34.5 | 8.4 | BOOL | set 1 if sent done
SBIT_1_5 | err_PBsend | M 34.6 | 8.5 | BOOL | Error during Profibus Transmission
SBIT_1_6 | err_PBrec | M 34.7 | 8.6 | BOOL | Error during Profibus Receive
SBIT_1_7 | PBrecd | M 35.0 | 8.7 | BOOL
SBIT_1_8 | PBrun | M 35.1 | 9.0 | BOOL
SBIT_1_9 | stop beam pulse | M 35.2 | 9.1 | BOOL | 1 sec pulse
SBIT_1_10 | start beam pulse | M 35.3 | 9.2 | BOOL | 1 sec pulse
outputs
O_BIT_0.I | repetition rate 1 Hz | A 8.0 | 12.0 | BOOL | to Laser, outputs, DB20 +16.0, MD42
O_BIT_1.I | repetition rate 10 Hz | A 8.1 | 12.1 | BOOL | to CS
O_BIT_2.I | pulse length 50 µs | A 8.2 | 12.2 | BOOL | to CS
O_BIT_3.I | pulse length 800 µs | A 8.3 | 12.3 | BOOL | to CS
O_BIT_4.I | op-mode cond set | A 8.4 | 12.4 | BOOL | to CS
O_BIT_5.I | op-mode gun set | A 8.5 | 12.5 | BOOL | to CS
O_BIT_6.I | op-mode analyse set | A 8.6 | 12.6 | BOOL | to CS
O_BIT_7.I | op-mode injector set | A 8.7 | 12.7 | BOOL | to CS
O_BIT_8.I | op-mode UV laser set | A 9.0 | 13.0 | BOOL | to CS
O_BIT_9.I | op-mode PP align set | A 9.1 | 13.1 | BOOL | to CS
O_BIT_10.I | RF enable | A 9.2 | 13.2 | BOOL | to CS
O_BIT_11.I | L-shutter enable | A 9.3 | 13.3 | BOOL | to Laser
O_BIT_12.I | Beam Stop | A 9.4 | 13.4 | BOOL | to CS
commands
BEAM_ENABLE | enable beam
BEAM_DISABLE | disable beam
RESET | unmask all bits
text variables
D_*.TI1 | text for state 1 |  |  | text
D_*.TI2 | text for state 2 |  |  | text
D_*.TD | description |  |  | text
S_*.TI | text for state |  |  | text
S_*.TD | description |  |  | text
O_*.TI | text for state |  |  | text
O_*.TD | description |  |  | text
value description
activ | 0
passiv | 1
DOOCS adress first Part
PITZ.I_LOCK/PBBIS/EBIS/