## Slide 1: In Water Operations in the 2025 / 26 Season, SpoolHub Power & EMI Reduction

## Slide 2: SpoolHub-Powering by Batteries
  Fully decouple the SpoolHub from the EMI generating spool-drive
  +/- 48 battery power over the slip ring
  miniPC powered by the mini-FBAP
Temp.
control
Charger
Heater
2x Battery
Slip ring
temperature-isolated box
110 VAC
SpooHub, by J. Kelley
12V

## Slide 3: Battery
Model DCHOUSE
17.21“ (440mm)
4.92“ (125mm)
13“ (330mm)

## Slide 4: Box
Model Zarges 40678

## Slide 5: Insulation
URSA XPS D N-III-L
125 x 6 x 3 cm
-50°C to +70°C
Extruded Polystyrol (XPS)
300 kPa at 10% compression

## Slide 6: Temperature Control
Model Silkwish 50 W

## Slide 7: Charger
Model YZ900

## Slide 8: Charger
Model Bauer 02-50

## Slide 9: Charger Switch
Model ANCLLO KAO-10KH

## Slide 10: Battery Box, Components
  preliminary
item | Manufacturer-ID | Remark
Box | Zarges 40678 | 600 x 400 x 340 mm
Insulation | Ursa XPS D N-III-L | Rigid foam, 30mm
Batteries | DCHOUSE 48V 50Ah | LiFePO4, Rechargeable battery with more than 4000 cycles, Built-in BMS (battery Management System), -20 to +55℃, 440 x 125 x 330 mm
Charger | Bauer LiFePO4 58.4 V 10 A | Fanless, Intelligent charging
Heating | Silkwish 50 W | with Thermostat - 52.5 x 25 cm
Switch | Kao-10KH | waterproof

## Slide 11: Spool Drive, EMI Filter
Model KEMET GTX (e.g.)
  To prevent the long spool drive cable acting as an antenna, causing EMI

## Slide 12: Conclusions for the in Water Operations
  big EMI related comms issues have been seen in the season 24/25
  Comms failed immediatly when the spool drive was running
  there is no realistic test setup in the North for testing the in water operations
  We should isolate the SpoolHub from the spool drive as much as possible
    Using batteries, we can cut any ground / shield connection to the spool drive
    Capacitive coupling by the slipring negligible?
  The battery based power supply can be built completely, by using off the shelf components
  the costs: ~2000 €
  Additionally, installing a good EMI filter in front of the spool drive would be useful
  Decision is needed soon!